## Introduction
Tune-up Report Building Energy Performance Program
1) All buildings conducting a tune-up to comply with the City of Philadelphia's Building Energy Performance Policy must submit documentation to the Office of Sustainability (OOS). This Tune-up Report template can be completed and submitted to meet this requirement. 2) Please read directions carefully and complete all the fields on all the tabs, accordingly. There are fields marked as "Optional" that are not required to be fully compliant. If a field is not applicable to a building, please use "N/A" or do not choose from a dropdown menu. 3) Instructions for the tune-up are located on the "Tune-up Instructions" tab. 4) The "Sign-off" tab must be completed and the Tune-up Specialist must be approved by OOS before this form is submitted to TuneUps@phila.gov. 5) Once completed, please send this report to "TuneUps@phila.gov" with the OPA # in the subject line.
Resources
1) Program Webpage
2) BEPP Regulations
3) BEPP Legislation
4) Tune-up Specialist Application
Please contact TuneUps@phila.gov with any question.

## Contact Information
Tune-up Report: City of Philadelphia's Building Energy Performance Program
Contact Information
Building Owner
|  | First Name | Last Name
|  | Company/Organization/LLC | Title
Mailing Address
|  | City | State | Zip
|  | Email Address | Phone Number
Primary Building Contact (can be "Same as Above")
Same contact as above?
|  | First Name | Last Name
|  | Company | Title
Mailing Address
|  | City | State | Zip
|  | Email Address | Phone Number
Additional Contact Information Notes (Optional)

## Building Overview
Tune-up Report: City of Philadelphia's Building Energy Performance Program
Building Overview
Building Information
Name
Address
|  | OPA # | Portfolio Manager ID #
|  | Primary Property Type | Define, if "Other"
Building Characteristics
General Information
|  | Year Built | Indoor Floor Space (Gross Sq. Ft.), excluding residential & parking
|  | Indoor Floor Space (Gross Sq. Ft.) including residential | Parking area (Sq. Ft.)
|  | # of Floors | # of Basements/Sub-basements
|  | Occupancy (% of total) | # of EV charging outlets
Fuel Sources Used
Electric
Gas
Steam
Fuel Oil
|  | On-site solar PV | Total kW installed:
Other (please define):
Building Automation System (BAS)
|  | Is there a BAS? | Type
|  | Brand/Manufacturer | Version
Comments about BAS (e.g. original building all pneumatic, X% converted to DDC)
Tenant Information
|  | Do tenants pay for their own energy use? | How is water metered in the building?
Does building management engage with tenants on energy efficiency opportunities?
If yes, provide a brief description of this program
Additional Building Notes (Optional)

## Other Major Systems & Equipment (hidden)
Tune-up Report: Building Energy Performance Policy
Other Major Systems & Equipment
Major Equipment - Centralized |  |  |  |  | Major Equipment - Decentralized (use sampling approach of at least 15%)
Equipment | Age | System Size Threshold | Unit of Measurement | Brief Description/Comment | Equipment | Age | System Size Threshold | Unit of Measurement | Brief Description/Comment
Other Major Systems
Equipment | Age | System Size Threshold | Unit of Measurement | Brief Description/Comment

## Major Spaces & Systems
Tune-up Report: City of Philadelphia's Building Energy Performance Program
Base Building Systems Inventory
Please include up to 5 of the largest energy using systems or spaces over 20,000 sq.ft (Ex. Data Center as other major use type).
No tenant of a covered building may deny reasonable access to a building owner or a tune-up specialist for purposes of compliance unless the Office of Sustainability provides an exemption for legitimate security concerns.
|  | Primary Use Type |  | Other Major Use Type |  | Other Major Use Type | Other Major Use Type | Other Major Use Type
|  | 1 |  | 2 |  | 3 | 4 | 5
Space Use
Size (Sq. ft.)
| Primary Heating System | Type |  | Type |  | Type | Type | Type
|  | Size |  | Size |  | Size | Size | Size
|  | Size (Unit) |  | Size (Unit) |  | Size (Unit) | Size (Unit) | Size (Unit)
|  | Age |  | Age |  | Age | Age | Age
|  | Efficiency Rating |  | Efficiency Rating |  | Efficiency Rating | Efficiency Rating | Efficiency Rating
|  | Efficiency Rating (Units) |  | Efficiency Rating (Units) |  | Efficiency Rating (Units) | Efficiency Rating (Units) | Efficiency Rating (Units)
|  | Condition |  | Condition |  | Condition | Condition | Condition
|  | General Schedule |  | General Schedule |  | General Schedule | General Schedule | General Schedule
|  | Setpoint |  | Setpoint |  | Setpoint | Setpoint | Setpoint
|  | Setback |  | Setback |  | Setback | Setback | Setback
|  | Notes |  | Notes |  | Notes | Notes | Notes
| Primary Cooling System | Type |  | Type |  | Type | Type | Type
|  | Equipment Size |  | Size |  | Size | Size | Size
|  | Size (Unit) |  | Size (Unit) |  | Size (Unit) | Size (Unit) | Size (Unit)
|  | Age |  | Age |  | Age | Age | Age
|  | Efficiency Rating |  | Efficiency Rating |  | Efficiency Rating | Efficiency Rating | Efficiency Rating
|  | Efficiency Rating (Units) |  | Efficiency Rating (Units) |  | Efficiency Rating (Units) | Efficiency Rating (Units) | Efficiency Rating (Units)
|  | Condition |  | Condition |  | Condition | Condition | Condition
|  | General Schedule |  | General Schedule |  | General Schedule | General Schedule | General Schedule
|  | Setpoint |  | Setpoint |  | Setpoint | Setpoint | Setpoint
|  | Setback |  | Setback |  | Setback | Setback | Setback
|  | Notes |  | Notes |  | Notes | Notes | Notes
| Primary Ventilation System | Type |  | Type |  | Type | Type | Type
|  | Equipment Size |  | Size |  | Size | Size | Size
|  | Size (Unit) |  | Size (Unit) |  | Size (Unit) | Size (Unit) | Size (Unit)
|  | Age |  | Age |  | Age | Age | Age
|  | Condition |  | Condition |  | Condition | Condition | Condition
|  | General Schedule |  | General Schedule |  | General Schedule | General Schedule | General Schedule
|  | Setpoint |  | Setpoint |  | Setpoint | Setpoint | Setpoint
|  | Setback |  | Setback |  | Setback | Setback | Setback
|  | Notes |  | Notes |  | Notes | Notes | Notes
| Primary Distribution System | Type |  | Type |  | Type | Type | Type
|  | Equipment Size |  | Size |  | Size | Size | Size
|  | Size (Unit) |  | Size (Unit) |  | Size (Unit) | Size (Unit) | Size (Unit)
|  | Age |  | Age |  | Age | Age | Age
|  | Condition |  | Condition |  | Condition | Condition | Condition
|  | General Schedule |  | General Schedule |  | General Schedule | General Schedule | General Schedule
|  | Setpoint |  | Setpoint |  | Setpoint | Setpoint | Setpoint
|  | Setback |  | Setback |  | Setback | Setback | Setback
|  | Notes |  | Notes |  | Notes | Notes | Notes
| Primary Domestic Hot Water System | Type |  | Type |  | Type | Type | Type
|  | Equipment Size |  | Size |  | Size | Size | Size
|  | Size (Unit) |  | Size (Unit) |  | Size (Unit) | Size (Unit) | Size (Unit)
|  | Age |  | Age |  | Age | Age | Age
|  | Condition |  | Condition |  | Condition | Condition | Condition
|  | General Schedule |  | General Schedule |  | General Schedule | General Schedule | General Schedule
|  | Setpoint |  | Setpoint |  | Setpoint | Setpoint | Setpoint
|  | Setback |  | Setback |  | Setback | Setback | Setback
|  | Notes |  | Notes |  | Notes | Notes | Notes
Primary Lighting Technology
Other Pumping and/or Electrical Systems
Notes
Other Major Equipment or Systems (Not referenced above)
| Systems/Equipment |  | Age | System Size Threshold | Size (unit) | Brief Description/Comment
Additional Major Systems Notes (Optional)

## Data Review
Tune-up Report: City of Philadelphia's Building Energy Performance Program
Data Reviews
Building Benchmarking
Review the property's most recent benchmarking submission in Portfolio Manager. Are the energy sources, square footage, property use details, and energy meter details listed correct?
If "No", please detail the errors below and make the necessary corrections.
Energy Bill Review
Review energy bills (monthly for past year, at least) for any abnormalities that could indicate poor or inappropriate functioning of systems and/or equipment. If found, include a summary of potential issues and further elaborate if specific tune-up items may be required to fix these issues.
|  | Start Date (of bills) | End Date (of bills)
Key Findings
Water Bill Review
Review water bills (monthly for past year, at least) for any abnormalities that could indicate poor or inappropriate functioning of systems and/or equipment. If found, include a summary of potential issues and further elaborate if specific tune-up items may be required to fix these issues.
|  | Start Date (of bills) | End Date (of bills)
Key Findings
Maintenance Review (Optional)
Review recent (e.g. last quarter) of tenant complaints regarding building systems and maintenance records. If complaints point to poor or inappropriate functioning of systems and/or equipment, include a summary of potential issues and further elaborate if specific tune-up items may be required to fix these issues.
|  | Start Date (of records) | End Date (of record)
Key Findings
Greenhouse (GHG) Gas Emissions (Optional)
If known by the building, or if the owner requests the calculation as part of the tune-up, provide the carbon emissions of the building
|  | Scope 1 Emissions (MTCO2e) | Scope 2 Emissions (MTCO2e)
Notes about GHG emissions

## Tune-Up Instructions
Tune-up Report: City of Philadelphia's Building Energy Performance Program
Tune-up Instructions
Tune-up Sections
Section 1) Building System Maintenance & Repairs
Section 2) HVAC Operations and Controls
Section 3) Lighting System Assessment
Section 4) Domestic Hot Water and Water Usage
Section 5) Building Envelope
Overarching Guidelines
• For assessment elements related to Maintenance & Repairs, building owners and Tune-Up Specialists should proceed according to ANSI/ASHRAE/ACCA Standard 180-2012 (or current edition). To learn more about how to become a Tune-Up Specialist, please review the application: https://www.phila.gov/media/20201123161214/BEPP-Tune-up-Specialist-Application.pdf • If a building does not contain a certain element or system associated with an Assessment Element, the Tune-Up Specialist should note this in the "Inspection Finding" and "Description of Extenuating Circumstances" columns, and also choose "N/A" in the "Deficiency?" column. No corrective action is required. • For any elements where a building owner can clearly demonstrate a reasoning for specific operations (e.g., meeting a specific use case, addressing a health issue, etc.), the owner may be exempt from completing the corrective action. The Tune-Up Specialist must still conduct an assessment and provide recommendations for the most efficient operation of that element, but the Specialist can approve the waiver of the corrective action by noting the reasoning in the "Description of Extenuating Circumstances" column. The Specialist should also choose "N/A" in the "Deficiency?" column. • Where a sampling is permitted, the Tune-Up Specialist can conduct a randomized inspection of at least 15% of that element, unless otherwise specified in the Assessment Overview column. Alternatively, rather than sampling 15% of an element, you may assess a representative sample of each zone throughout the entire building. Within the "Sampling Approach" column, the Tune-Up Specialist must note the number of elements included in the random inspection, the total number of elements in the building (can be estimated), and the number of floors (as a % of total) on which an element was inspected. • If over 50% of sampled elements demonstrate need for corrective actions, the Tune-Up Specialist should provide a recommendation to the building owner in the "Corrective Action Description" column about if (and how) to review and/or correct potential issues among the broader set of the elements throughout the building. Corrective action on elements outside the sampling range is voluntary. The building owners should provide to the Tune-Up Specialist a description of further steps beyond fixing the sampled elements, if any, the building will take. The Tune-Up Specialist should note this within the "End Condition/Current Condition" column and describe what, if anything, was completed during the final review. • After corrective actions are completed, Tune-Up Specialists must reassess all elements that are both marked "Yes" in the "Deficiency?" cell and require a corrective action. Tune-Up Specialists only have to reassess elements with voluntary corrective actions if the building takes action.
Tune-up Section Guidance
| Action # | Assessment Element | Inspection Overview | Corrective Action | Inspection Finding | Deficiency? | Sampling Approach (If Applicable) | Corrective Action Description (If Applicable) | End Condition/Current Condition | Description of Extenuating Circumstances (If Applicable)
| These cells do not require any action. They provide descriptions of the elements to be assessed and what the Tune-Up Specialist should consider during the assessment. |  |  | Green cells: The corrective action is required to be completed if a deficiency is found. | The Tune-Up Specialist should provide a brief overview of what the assessment found and how the element is functioning in relation to the "Inspection Overview" prompt. | The Tune-Up Specialist should: • Choose the appropriate "Yes" options to signal that a deficiency was found. • Choose "No" if the element is functioning optimally • Choose "N/A" if the element is not in the building or if there are extenuating circumstances. | The Tune-Up Specialist should briefly describe the sampling approach taken, if applicable, to an element. This should include at least the number of elements included in the random sample, the total number of elements in the building (can be estimated), and the number of floors (as a % of total) on which an element was inspected. | The Tune-Up Specialist should briefly describe the action(s) recommended to remedy the deficiency. It should provide additional detail and specificity to the language in the "Corrective Action" cell. | The Tune-Up Specialist should briefly describe the end condition of an element following the corrective action phase of the tune-up. If nothing was altered, please write "current condition". Also, if applicable, please note if the building failed to take corrective action when required. | The Tune-Up Specialist should provide an explanation in this box if: • An element does not exist within the building and therefore cannot be assessed or corrected. • "N/A" was chosen for the "Deficiency?" column because the building provides a sufficient reason for the Tune-Up Specialist to waive a corrective action.
Yellow cells: The corrective action is voluntary if a deficiency is found.
Please contact TuneUps@phila.gov with any questions about the tune-up.

## 1) Maintenance & Repairs
Tune-up Report: City of Philadelphia's Building Energy Performance Program
Maintenance & Repairs: Tune-up Actions
| Action # | Assessment Element | Inspection Overview | Sampling Allowed | Corrective Action | Inspection Finding | Deficiency? | Sampling Approach (If Applicable) | Corrective Action Description (If Applicable) | End Condition/Current Condition | Description of Extenuating Circumstances (If Applicable)
| 1.1 | Grilles and Coils | Inspect a sampling of grilles and coils. | Yes | Clean and maintain where impacting system performance.
| 1.2 | Filters | Inspect a sampling of filters to determine if clean and regularly maintained. | Yes | Clean and maintain where impacting system performance.
| 1.3 | Strainers | Inspect sampling of strainers to determine if clean and regularly maintained. | Yes | Clean and maintain where impacting system performance.
| 1.4 | Motors and Belts | Inspect sampling of motors and belts. | Yes | Clean and maintain where impacting system performance.
| 1.5 | Filters, Strainers, Motors, Belts | If scope of work to rectify deficiencies found in 1.2, 1.3, and 1.4 is more than standard or regular maintenance, recommend repairs. | No | Implement repairs.
| 1.6 | Dampers and valves | Inspect sampling of dampers and valves for proper functionality, including opening and closing fully. | Yes | Repair as needed where impacting system performance.
| 1.7 | Variable frequency drive (VFD) | Review the modes for any VFDs. | No | Place VFDs in "Auto" mode. Adjust BAS or controls as appropriate for system performance.
| 1.8 | Service Life of Major Equipment | Identify equipment approaching the end of its service life, per ASHRAE Service Life Database. Recommend replacement plan and schedule. | No | Implement replacement plan and schedule
| 1.9 | Visible Ducts and pipes | Inspect ducts and pipes that are visible and make recommendations for where new insulation or repair to existing insulation would enhance system performance. This should include steam pipes. Provide indicative pricing for insulation and/or repairs in these locations. | No | Implement recommendations for insulating or repairing pipes and/or ducts.
| 1.10 | Steam Traps | Inspect the main steam traps to determine if they have failed. | No | Replace failed steam traps, if any.
Tune-up Specialist Notes (Optional)

## 2) HVAC
Tune-up Report: City of Philadelphia's Building Energy Performance Program
HVAC: Tune-up Actions
| Action # | Assessment Element | Inspection Overview | Sampling Allowed | Corrective Action | Inspection Finding | Deficiency? | Sampling Approach (If Applicable) | Corrective Action Description (If Applicable) | End Condition/Current Condition | Description of Extenuating Circumstances (If Applicable)
| 2.1 | Occupancy Scheduling, Temperature Setbacks and Supply Fan Cycling | Review HVAC equipment schedules (Including daily, weekly, seasonal, day/night, occupied/unoccupied hours). Review HVAC set points (including space temperatures, supply air temperatures, CO2, economizer changeover temperatures, supply fan cycling and static pressure). Compare actual readings of relevant data points from a representative sample of elements to ensure the set points are being met. | Yes | Set schedules and setpoints as appropriate to support building use, occupancy patterns, and occupant needs.
| 2.2 | Temperature and Static Pressure Resets: Hot Water, Chilled Water, Distribution Air Temperature | Review reset schedules (including supply air temperature, supply air pressure, boiler and chiller water temperature, lockouts with outside air temperature, loop differential pressure). | No | Establish or adjust schedules as appropriate to support efficient operations.
| 2.3 | Economizer Mode, Demand Controlled Ventilation, and/or Minimum Outside Air Controls | Review minimum outside air controls, including demand controlled ventilation and OA controls for economizer mode, to verify ventilation rates do not vary significantly from rates specified in ASHRAE 62.1 Standards for current facility type. | No | Correct and repair equipment in areas where ventilation rates vary significantly from ASHRAE 62.1 Standards and are inappropriate for current facility requirements (e.g. no outside air supply or 100% outside air supply, etc.).
| 2.4 | Optimal Start/Stop | Review optimal start/stop capabilities | No | Establish or confirm optimal start/stop capabilities as appropriate to support the building use and occupant needs.
| 2.5 | Simultaneous Heating and Cooling | Review HVAC controls for unintended or inappropriate instances of simultaneous heating and cooling. | No | Adjust HVAC controls to reduce or eliminate any unintended or inappropriate simultaneous heating and cooling.
| 2.6 | Major Equipment Sensors | Verify that HVAC sensors are functioning, calibrated, and in appropriate locations. Sensors may include, but are not limited to, zone temperature; outside air/return-air temperature; mixed air/discharge air temperature; pressure; occupancy; humidity. The assessment can include a sampling of sensors and must group like sensors (e.g. discharge, space, etc.) to meet the 15% sampling floor. | Yes | Repair, adjust, move in close proximity or recalibrate as appropriate.
| 2.7 | HVAC Controls | Verify HVAC controls are functioning as intended for building operation. | No | Adjust control sequences as appropriate for current facility requirements.
| 2.8 | Exhaust fans | Inspect exhaust fans to determine if they are functioning and if controls (e.g. schedule or sensor) are properly calibrated. | No | If deficiency found, adjust schedule, fix sensor, and/or repair fan.
| 2.9 | Central Plant Operations | If a Central Heating and/or Cooling Plant exists, review the operations. Review HVAC set points (boiler supply and return temperatures, chilled water supply and return temperatures, condenser water supply and return temperatures, water or steam system pressures, and equipment sequencing). | No | Set schedules (including seasonal shutdowns) and setpoints as appropriate to support building use, occupancy patterns and occupant needs.
| 2.10 | Air Balancing Issues | Note any indications of significant air-balancing issues (e.g. wind-tunnel effect). | No | Recommend rebalancing of HVAC air and water systems where significant efficiency or comfort improvements can be achieved.
| 2.11 | Dominant Zones | Identify zones that are dominating multi-zone system operations, and that cause inefficiencies and/or comfort issues. Recommend solutions to isolate these zones. | No | Implement recommendations.
| 2.12 | Cooling Tower Fan Operation | If cooling tower is two cell or greater, review fan operation. Determine whether fans are running in parallel or in sequence, and recommend running in parallel unless cooling tower configuration requires sequence operation. | No | Implement recommendations.
| 2.13 | Variable frequency drive (VFD) applications | Identify areas that could benefit from variable frequency drives; identify pump and fan motors that are prime candidates for VFD upgrades. | No | Implement recommendations.
Tune-up Specialist Notes (Optional)

## 3) Lighting
Tune-up Report: City of Philadelphia's Building Energy Performance Program
Lighting: Tune-up Actions
| Action # | Assessment Element | Inspection Overview | Sampling Allowed | Corrective Action | Inspection Finding | Deficiency? | Sampling Approach (If Applicable) | Corrective Action Description (If Applicable) | End Condition/Current Condition | Description of Extenuating Circumstances (If Applicable)
| 3.1 | Lighting Control Schedules and Sequences | Review lighting controls, schedules and sequences (including daily, weekly, seasonal, day/night, occupied/unoccupied hours). | No | Set schedules and controls so they appropriately match building use, occupancy patterns and occupant needs, and limit wasted energy to the extent possible.
| 3.2 | Light Levels | Identify areas where lighting levels are significantly higher than appropriate for the space use and occupancy needs. Recommend dimming, delamping or other options to improve lighting to support building use and occupant needs. | No | Implement options recommended to adjust for appropriate lighting levels.
| 3.3 | Inefficient Lighting and Sensors | Identify low-cost lighting energy conservation measures that would enhance system performance (specifically inefficient incandescent, fluorescent, or metal halide lighting; and opportunities for lighting controls). Provide indicative pricing for the proposed solutions. | No | Implement low-cost light energy conservations measures.
| 3.4 | Functional Lighting Sensors | Where installed, verify lighting sensors are working as designed. | No | Repair any malfunctioning lighting sensors.
Tune-up Specialist Notes (Optional)

## 4) DHW & Water
Tune-up Report: City of Philadelphia's Building Energy Performance Program
Domestic Hot Water & Water Usage: Tune-up Actions
| Action # | Assessment Element | Inspection Overview | Sampling Allowed | Corrective Action | Inspection Finding | Deficiency? | Sampling Approach (If Applicable) | Corrective Action Description (If Applicable) | End Condition/Current Condition | Description of Extenuating Circumstances (If Applicable)
| 4.1 | Domestic Hot Water | Review domestic hot water setpoints to determine if the current setpoints are appropriate for the buildings use cases. | No | Lower setpoints to the minimum temperature possible that will not adversely affect operations.
| 4.2 | Circulation pumps | Review circulation pumps to ensure they function and set according to ANSI/ASHRAE/ACCA Standard 180-2012 (or current edition). | No | If not functioning, fix the circulation pumps. If not set to meet to ANSI/ASHRAE/ACCA Standard 180-2012 (or current edition), adjust as appropriate.
| 4.3 | Plumbing Fixtures | Either: 1) Inspect 10% of plumbing fixtures for leaks or other maintenance needs. Expand inspection to 20% if deficiencies found in 50% or more of a specific type of fixture. OR 2) Review a comprehensive maintenance report of fixtures kept by on-site staff to determine any potential maintenance needs (must show at least quarterly inspection). | Yes | Conduct standard or regular maintenance actions on fixtures requiring repair.
| 4.3.1 | Plumbing Fixtures | If scope of work to rectify deficiencies found in 4.3 is more than standard maintenance (e.g., replacement of entire fixtures) recommend repairs. | No | Implement recommended repairs.
| 4.4 | Cooling Tower | Evaluate cooling towers for water leaks and excess water consumption. Also verify that cooling tower conductivity meter used to control blow down is calibrated and functioning properly. | No | Repair any leaks and address excess water consumption. Calibrate meter appropriately.
| 4.4.1 | Cooling Tower | If evaluation returns any deficiencies that fall beyond normal maintenance, recommend repairs | No | Implement repairs
| 4.5 | Water Usage setpoints and controls | Review makeup water controls for temperature control (including cooling tower makeup water) and irrigation systems. | No | Adjust setpoints and controls as necessary to improve efficiency.
| 4.6 | Water Features | Review water feature schedules to ensure they shut-down during night-time or unoccupied periods, where appropriate | No | Implement scheduling changes
| 4.7 | Water flow fixtures | Check for use of low flow fixtures and aerators. Assessment may be based on a random sampling of at least 5% of each type of fixture. | Yes | Install low flow fixtures and/or aerators, as appropriate.
Tune-up Specialist Notes (Optional)

## 5) Envelope
Tune-up Report: City of Philadelphia's Building Energy Performance Program
Building Envelope: Tune-up Actions
| Action # | Assessment Element | Inspection Overview | Sampling Allowed | Corrective Action | Inspection Finding | Deficiency? | Sampling Approach (If Applicable) | Corrective Action Description (If Applicable) | End Condition/Current Condition | Description of Extenuating Circumstances (If Applicable)
| 5.1 | Roof condition | Check for roof penetrations, gaps, and/or damage that could allow for the entry of air or water (such as at dampers or top of elevator shaft). | No | Repair issues, as appropriate.
| 5.2 | Roof and Wall Insulation | Identify and recommend insulation in areas impacting system performance that are outside of a standard or regular maintenance action. Recommend Cool Roof coating where appropriate. | No | Implement recommendations.
| 5.3 | Windows and doors | Inspect age and condition of windows. Inspect both windows and doors for seals, weatherstripping, etc. Identify and recommend repairs impacting system performance that are outside of a standard or regular maintenance action. Inspection only required for a representative sample of doors and windows. | Yes | Implement recommendations.
Tune-up Specialist Notes (Optional)

## Tune-up Summary
Tune-up Report: Philadelphia's Building Energy Performance Program
Tune-up Summary
Tune-up Dates
|  |  | Start Date (Assessment) |  | End Date (Assessment) | Date(s) of Reassessment
Greatest Impact - Required Actions
A brief description of at least five (5) required actions, listed by greatest projected impact:
|  |  | Action | Description
1)
2)
3)
4)
5)
6)
7)
Greatest Impact - Recommended Actions
A brief description of at least five (5) recommended actions, listed by greatest projected impact:
|  |  | Action | Description
1)
2)
3)
4)
5)
6)
7)

## Sign-off
Tune-up Report: Philadelphia's Building Energy Performance Program
Tune-Up Sign Off & Certification
Tune-up Specialist Information
|  | First Name | Last Name
|  | Company/Affiliation | Title |  | PE and/or CEM #
Mailing Address
|  | City | State |  | Zip
|  | Email Address | Phone Number
Certifications
| 1) | I certify that I supervised a tune-up assessment at building |  |  | 0
| 2) | I certify that I reviewed and confirmed the corrective actions at building |  |  | 0
| 3) | I certify that the requirements of the Policy have been met by building |  |  | 0
| 4) | I certify that I have shared this report with the owner(s) of building |  |  | 0
| 5) | I certify that I followed the requirements of the Policy to the best of my ability and that I have not knowingly misled or misrepresented anything within this report.
|  | Signature |  | Date

## Dropdowns (hidden) (hidden)
City Designated Property Type | States | Y/N | % | Space Uses | BAS | Deficiency | Water Meter | Records | Age | Condition | Heating Systems | Heating Systems (v2) | Cooling Systems | Cooling Systems (v2) | Primary Ventilation System | Primary Ventilation System (v2) | Primary Distribution System | Primary Distribution System (v2) | Primary Hot Water | Primary Hot Water | Primary Lighting Technology | Primary Lighting Technology (v2) | Other Major Systems | Major Equipment - centralized | Major Equipment - Decentralized (use sampling approach of at least 15%) | Tenant Energy | Rating Systems - Cooling | Rating Systems - Heating
Adult Education | AK | Yes | 0-10 | Adult Education | Direct Digital Control | Deficiency found; corrective action required | Master metered | Yes, tenant complaints | 0-5 | New | Boiler - Electric | Same as above | California Heat Pump Loop | Same as above | Natural Ventilation (>4% operable area/floor area) | Same as above | Air Handler Unit Multi Zone | Same as above | Gas water heating tank(s) | Same as above | Incandescent - Edison/Standard | Same as above | ***Major Systems*** | Boilers | Window Units | Yes, they pay for gas | SEER | AFUE
College/University | AL | No | 11-20 | Ambulatory Surgical Center | Pneumatic | Deficiency found; corrective action voluntary | Tenants metered separately | Yes, maintenance records | 6-10 | Good | Boiler - Gas | Boiler - Electric | Chiller Plant | California Heat Pump Loop | 100% Outside Air | Natural Ventilation (>4% operable area/floor area) | Air Handler Unit Single Zone | Air Handler Unit Multi Zone | Electric water heating tank(s) | Gas water heating tank(s) | Incandescent - Halogen | Incandescent - Edison/Standard | Hot Water Heating Plant | Air Handling Units | Unit Heaters | Yes, they pay for electric | EER | HSPF
Commercial | AR |  | 21-30 | Aquarium |  | No deficiency found |  | Yes, both | 11-15 | Fair | Boiler - Other | Boiler - Gas | Direct Expansion Split System | Chiller Plant | Dedicated Outdoor Air System | 100% Outside Air | Constant Volume AHU | Air Handler Unit Single Zone | Heat Pump water heating tank(s) | Electric water heating tank(s) | Fluorescent T5 | Incandescent - Halogen | Steam Heating Plant | Cooling Towers | Packaged RTUs (Single Zone, Multizone, VAV, etc) | Yes, they pay for gas and electric | HSPF | Et
Data Center | AZ |  | 31-40 | Athletic Fields |  | N/A |  | No | 16-20 | Poor | California Heat Pump Loop | Boiler - Other | Direct Expansion Window AC Unit | Direct Expansion Split System | Demand Controlled Ventilation (CO2 or other) | Dedicated Outdoor Air System | Constant Volume AHU with zone heating coils | Constant Volume AHU | Solar water heating tank(s) with gas backup | Heat Pump water heating tank(s) | Fluorescent T8 | Fluorescent T5 | District Steam | Fan Coil Units | Makeup Air Unit | No | COP | Other (specify in notes)
Distribution | CA |  | 41-50 | Automobile Dealership |  |  |  |  | 21-25 | End of life | Constant Volume AHU | California Heat Pump Loop | District Chilled Water Cooling Plant | Direct Expansion Window AC Unit | Exhaust Only with Passive Make-up Air | Demand Controlled Ventilation (CO2 or other) | Fan Coils - Hot Water | Constant Volume AHU with zone heating coils | Solar water heating tank(s) with electric backup | Solar water heating tank(s) with gas backup | Fluorescent T12 | Fluorescent T8 | District Cooling | Chillers (Air and Water Cooled) | Decentralized Heat pumps and Split systems (Airsource) |  | kW/ton
Hospital | CO |  | 51-60 | Bank Branch |  |  |  |  | 25+ | Not functioning | Constant Volume AHU with Zone Heating Coils | Constant Volume AHU | Ductless Heat Pump | District Chilled Water Cooling Plant | Fixed Outside Air Damper | Exhaust Only with Passive Make-up Air | Fan Coils - Refrigerant | Fan Coils - Hot Water | Central Gas Boiler for Water Heating | Solar water heating tank(s) with electric backup | LED | Fluorescent T12 | Chilled Water Plant | Rooftop Units served in part from Central Plant (Single Zone, Multizone, VAV, etc) | PTAC or PTHP (Packaged Terminal Units) |  | Other (specify in notes)
Hotel | CT |  | 61-70 | Bar/Nightclub | [6 empty] | District Hot Water Plant | Constant Volume AHU with Zone Heating Coils | Evaporative Cooler | Ductless Heat Pump | Heat Recovery or Energy Recovery Ventilation | Fixed Outside Air Damper | Fan Coils - Steam | Fan Coils - Refrigerant | Central Oil Boiler for Water Heating | Central Gas Boiler for Water Heating | Compact Fluorescent | LED | Humidification System | Centralized Heat pumps (Air and Water-source including Variable Refrigerant Flow)
Industrial | DC |  | 71-80 | Barracks | [6 empty] | District Steam Plant | District Hot Water Plant | Heat Pump Air Source Split System | Evaporative Cooler | Other | Heat Recovery or Energy Recovery Ventilation | Forced Air Fan | Fan Coils - Steam | Central Boiler for Combined Space and Water Heating | Central Oil Boiler for Water Heating | Metal Halide | Compact Fluorescent | Energy Recovery Loops | Heatexchanger (Heating or Cooling)
Laboratory | DE |  | 81-90 | Bowling Alley | [6 empty] | Ductless Heat Pump | District Steam Plant | Heat Pump Air Source Variable Refrigerant Flow | Heat Pump Air Source Split System |  | Other | Packaged VAV | Forced Air Fan | On Demand Gas Water Heater | Central Boiler for Combined Space and Water Heating | High-Pressure Sodium | Metal Halide | Ventilation Systems
Manufacturing | FL |  | 91-100 | Casino | [6 empty] | Electric Resistance Baseboard, Cabinet Heater | Ductless Heat Pump | Heat Pump Ground Source | Heat Pump Air Source Variable Refrigerant Flow |  |  | Powered Induction Terminal Unit | Packaged VAV | On Demand Electric Water Heater | On Demand Gas Water Heater | Mercury Vapor | High-Pressure Sodium | Domestic Hot Water Heating
Medical Office | GA |  |  | College/University | [6 empty] | Furnace - Electric | Electric Resistance Baseboard, Cabinet Heater | Heat Pump Water Source | Heat Pump Ground Source |  |  | Radiant Electric Baseboard or Surface | Powered Induction Terminal Unit | Waste Heat exchange system | On Demand Electric Water Heater | Other | Mercury Vapor | On-site Power Generation
Mixed Use | HI |  |  | Convenience Store with Gas Station | [6 empty] | Furnace - Gas | Furnace - Electric | Packaged Rooftop Unit | Heat Pump Water Source |  |  | Radiators - Hot Water | Radiant Electric Baseboard or Surface | Steam Heat exchange system | Waste Heat exchange system | Unknown | Other | Energy Storage Systems
Municipal | IA |  |  | Convenience Store without Gas Station | [6 empty] | Heat Pump Air Source Split System | Furnace - Gas | Packaged Terminal AC | Packaged Rooftop Unit |  |  | Radiators - Steam | Radiators - Hot Water | Other | Steam Heat exchange system |  | Unknown | ***Major Equipment -Centralized***
Museum | ID |  |  | Convention Center | [6 empty] | Heat Pump Air Source Variable Refrigerant Flow | Heat Pump Air Source Split System | Packaged Terminal HP | Packaged Terminal AC |  |  | Reheat Terminal Unit Electric | Radiators - Steam | No DHW System | Other |  |  | Boilers
Nightclub | IL |  |  | Courthouse | [6 empty] | Heat Pump Ground Source | Heat Pump Air Source Variable Refrigerant Flow | Other - please describe in Notes column | Packaged Terminal HP |  |  | Reheat Terminal Unit Gas | Reheat Terminal Unit Electric |  | No DHW System |  |  | Air Handling Units
Office | IN |  |  | Data Center | [6 empty] | Heat Pump Water Source | Heat Pump Ground Source | No Cooling | Other - please describe in Notes column |  |  | Other | Reheat Terminal Unit Gas |  |  |  |  | Cooling Towers
Other | KS |  |  | Distribution Center | [6 empty] | Make-up Air Unit - Electric | Heat Pump Water Source |  | No Cooling |  |  | No Distribution System | Other |  |  |  |  | Fan Coil Units
Retail | KY |  |  | Drinking Water Treatment & Distribution | [6 empty] | Make-up Air Unit - Gas | Make-up Air Unit - Electric | [5 empty] | No Distribution System |  |  |  |  | Chillers (Air and Water Cooled)
School (K-12) | LA |  |  | Enclosed Mall | [6 empty] | Packaged Terminal HP | Make-up Air Unit - Gas | [10 empty] | Rooftop Units served in part from Central Plant (Single Zone, Multizone, VAV, etc)
Supermarket | MA |  |  | Energy/Power Station | [6 empty] | Packaged VAV - Electric Reheat | Packaged Terminal HP | [10 empty] | Centralized Heat pumps (Air and Water-source including Variable Refrigerant Flow)
Warehouse | MD |  |  | Fast Food Restaurant | [6 empty] | Packaged VAV - Gas Reheat | Packaged VAV - Electric Reheat | [10 empty] | Heatexchanger (Heating or Cooling)
Worship | ME |  |  | Financial Office | [6 empty] | Packaged VAV - Hot Water | Packaged VAV - Gas Reheat | [10 empty] | ***Major Equipment - Decentralized***
| MI |  |  | Fire Station | [6 empty] | PRTU - Gas | Packaged VAV - Hot Water | [10 empty] | Window Units
| MN |  |  | Fitness Center/Health Club/Gym | [6 empty] | PRTU - Heat Pump | PRTU - Gas | [10 empty] | Unit Heaters
| MO |  |  | Food Sales | [6 empty] | Unit Heater - Electric | PRTU - Heat Pump | [10 empty] | Packaged RTUs (Single Zone, Multizone, VAV, etc)
| MS |  |  | Food Service | [6 empty] | Unit Heater - Gas | Unit Heater - Electric | [10 empty] | Makeup Air Unit
| MT |  |  | Hospital (General Medical & Surgical) | [6 empty] | No heating | Unit Heater - Gas | [10 empty] | Decentralized Heat pumps and Split systems (Airsource)
| NC |  |  | Hotel | [6 empty] | Other | No heating | [10 empty] | PTAC or PTHP (Packaged Terminal Units)
| ND |  |  | Ice/Curling Rink | [7 empty] | Other
| NE |  |  | Indoor Arena
| NH |  |  | K-12 School
| NJ |  |  | Laboratory
| NM |  |  | Library
| NV |  |  | Lifestyle Center
| NY |  |  | Mailing Center/Post Office
| OH |  |  | Manufacturing/Industrial Plant
| OK |  |  | Medical Office
| OR |  |  | Mixed Use Property
| PA |  |  | Movie Theater
| RI |  |  | Multifamily Housing
| SC |  |  | Museum
| SD |  |  | Non-Refrigerated Warehouse
| TN |  |  | Office
| TX |  |  | Other
| UT |  |  | Other – Education
| VA |  |  | Other – Entertainment/Public Assembly
| VT |  |  | Other – Lodging/Residential
| WA |  |  | Other – Office
| WI |  |  | Other – Other
| WV |  |  | Other – Public Service
| WY |  |  | Other – Recreation
| GU |  |  | Other – Restaurant/Bar
| MH |  |  | Other – Retail/Mall
| MP |  |  | Other – Services
| PR |  |  | Other – Specialty Hospital
| VI |  |  | Other – Stadium
Other – Technology/Science
Other – Utility
Outpatient Rehabilitation/Physical Therapy
Parking
Performing Arts
Personal Services (Health/Beauty, Dry Cleaning, etc.)
Police Station
Pre-school/Daycare
Prison/Incarceration
Race Track
Refrigerated Warehouse
Repair Services (Vehicle, Shoe, Locksmith, etc.)
Residence Hall/Dormitory
Residential Care Facility
Restaurant
Retail Store
Roller Rink
Self-Storage Facility
Senior Care Community
Single Family Home
Social/Meeting Hall
Stadium (Closed)
Stadium (Open)
Strip Mall
Supermarket/Grocery Store
Swimming Pool
Transportation Terminal/Station
Urgent Care/Clinic/Other Outpatient
Veterinary Office
Vocational School
Wastewater Treatment Plant
Wholesale Club/Supercenter
Worship Facility
Zoo

## Dropdowns - HP (hidden) (2) (hidden)
Pathways
*Fills automatically based on dropdown menu above*
LEED for Building Operations & Maintenance v.4 (Gold or Platinum) | 1) LEED certificate for Building Operations and Maintenance (O & M) issued by United States Green Building Council (USGBC). 2) LEED scorecard. 3) This completed form.
Net-Zero Energy Certification | 1) Net-Zero Energy Certification issued by International Living Future Institute (ILFI), with any summary documentation. 2) This completed form.
Utility retro-commissioning program | 1) Documentation, including final approval by PECO, that provides evidence of completed whole building retrocommissioning, as defined in Pennsylvania Act 129 of 2008 as amended or subsequently altered for additional phase. 2) This completed form.
Full retro- or recommissioning procedure | 1) Documentation by the provider who conducted the retrocommissioning or recommissioning demonstrating (a) that it covered at least seventy-five percent (75%) of the Covered Building’s square footage and (b)that it met the energy reduction requirements promulgated in Phase 3 of Act 129 (at least 300 kWh per square foot). 2). This completed form.
15% Energy Savings | 1) ENERGY STAR Statement of Performance (SEP) for three calendar years evidencing a site EUI reduced fifteen percent (15%) compared to the highest weather-normalized EUI in the three referenced calendar years prior to the Tune-up date. 2) A cover letter verifying the accuracy of the reporting and signed by any person possessing the qualifications of a Specialist. 3) This completed form. *For building owners pursuing the 15% energy savings pathway may request a non-guaranteed extension one year to submit the required documentation. No sooner than 180 days prior to the Compliance Deadline, the owner shall provide in writing and in a form acceptable to the OOS, evidence sufficient to the OOS that the building will meet the exemption requirement, and if the application fails the Covered Building shall conduct a Tune-up within one year of the date of its exemption denial.
15% Energy Savings (using C-PACE Financing) | 1) For C-PACE certification, the verification by the Philadelphia C-PACE Program Administrator regarding the annual energy savings projection approved as part of the building’s C-PACE financing, if C-PACE financing was used for the reduction. 2) This completed form
Low Site EUI | 1) A copy of the Statement of Energy Performance (SEP) for each of the qualifying years demonstrating a weather-normalized site EUI equal to or less than twenty (20) kBTU/sq for at least two of the three preceding calendar years to the Compliance Date. 2) Written validation of the SEP data by any person with Specialist qualifications. 3) This completed form.
ENERGY STAR Certification | 1) Either (a) a copy of the EPA-issued ENERGY STAR Certificate of Achievement or (b) the congratulatory email confirming certification. 2) Either (a) a copy of the application for Certification or (b) the Statement of Energy Performance (SEP) with the same year-ending date as the application. 3) This completed form. * For tune-ups scheduled in calendar years 2021 and 2022: A 2019 ENERGY STAR Certification will be accepted for buildings with a Compliance Deadline in 2021 and 2022 to be exempt from the tune-up requirement. To qualify for the 2019 ENERGY STAR exemption, owner(s) shall submit (1) either a copy of the EPA-issued ENERGY STAR Certificate of Achievement or (2) the congratulatory email confirming certification; and either (1) a copy of the application for Certification or (2) the Statement of Energy Performance (SEP) with the same year-ending date as the application. This provision shall expire on December 31, 2022.
Manual Ongoing Commissioning | 1) On-going commissioning plan (with all the elements required in LEED Operations and Maintenance v4 (or current edition) Ongoing Commissioning Energy and Atmosphere credit). 2) One year of quarterly (or more frequent) reports that detail findings from efforts and corrections made. 3) This completed form.
Automated Active Optimization (CCx) | 1) Description of the system(s) 2) One year of quarterly (or more frequent) reports generated by the automated system that include: (a).Faults/issues detected; (b) Date of each fault/issue was detected; (c) Date of correction/repair for each fault/issue, if corrected/repaired; (d)Staff/vendor notes on what was done to remedy each fault/issue (optional). 3) This complete form. NOTE: If base-building lighting systems are not covered by the automated system, Owner may submit alternative documentation to demonstrate manual ongoing commissioning. This documentation can either be an ongoing commissioning plan and reports as referenced in Section 7.d.vi.i or a written description of the protocols to ensure lighting systems and their use reflect the occupant and space needs. *For tune-ups scheduled in calendar years 2021 and 2022: For building owners pursuing the active optimization pathway may, upon application and no sooner than 180 days prior to the Compliance Deadline and approval by OOS, receive an extension of no more than two years from the Compliance Deadline to implement the Active Optimization and collect relevant data. Extension applications under this subsection include: Description of the type of program; Systems to be actively optimized; Timeline for launch and data qualification; and Verification by a person possessing Specialist qualifications.
Energy Audit | 1) An audit report and cover letter signed by the energy audit lead of an ASHRAE Level II Commercial Building Energy Audit (or equivalent). This letter must list all the no-cost/low-cost energy efficiency measures (defined as providing a simple payback of three years or less) identified in the audit and verify implementation of these measures. 2) This completed form.

## Data (hidden) (hidden)
To be developed